{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["Ark1","Ark2","Ark3"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Ark1","index":0,"n_rows":30,"n_cols":75,"rows_kept":30,"cut":false,"hidden":false,"merged":[[2,7,2,8],[3,11,3,12],[2,2,2,5],[24,0,24,8],[8,0,10,0],[3,2,3,5],[4,2,4,5],[3,7,3,8]]}
[null,null,"DE DANSKE GASSELSKABER",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Tryktab pr. meter"]
[null,null,null,null,null,null,null,"VERSION 1 / 07.09.2010/lbr",null,null,"Indtast i grønne felter i tabellen"]
["Projekt.nr. (eller navn):",null,null,null,null,null,"Dato:",{"$f":"TODAY()","v":"2010-11-30"},null,null,null,null,null,null,null,null,null,null,null,"Luft"]
["Installationsnr.:",null,null,null,null,null,"Ref.:",null,null,null,null,""]
["Beskrivelse:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dimension [mm]","Flow [m³/h]"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.2,0.3,0.4,0.5,0.6,0.7,0.8,0.9,1,1.1000000000000001,1.2,1.3,1.4,1.5,1.6,1.7,1.8,1.9,2,2.1,2.2000000000000002,2.2999999999999998,2.4,2.5,2.6,2.7,2.8,2.9,3,3.2,3.4,3.6,3.8,4,4.2,4.4000000000000004,4.5999999999999996,4.8,5,5.2,5.4,5.6,5.8,6,6.2,6.4,6.6,6.8,6.9999999999999902,7.5,8,8.5,9,9.5,10]
["Tryktabsberegning for CSST-rør (Fleksible rustfri stålrør)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,1.52,2.4500000000000002,3.72,5.39,9.6,14.7,19.600000000000001,25.28,31.85,39.200000000000003,47.04,56.35,66.64,77.42]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,1.08,1.33,1.72,2.21,2.94,4.3099999999999996,6.57,8.7200000000000006,10.58,12.54,14.7,16.86,19.5,22.05,24.79,27.54,30.87,33.81,37.24,41.16,45.08,49,52.43,56.84,60.76,64.680000000000007,69.58,74.48]
["Stræk\neller \nberegning","Belastning\n(HØ)","Nom.\nvol.strøm","Rørdiam. Nom.","Gashast.","Længde","Tryktab\npr. meter","Tryktab for \ndenne længde","Samlet\ntryktab ",null,null,null,null,null,null,null,null,null,null,20,null,null,null,null,null,null,0.98,1.18,1.37,1.57,1.86,2.25,2.84,3.53,4.0199999999999996,4.6100000000000003,5.0999999999999996,5.68,6.27,6.86,7.55,8.1300000000000008,8.82,9.6,10.29,11.07,11.96,12.74,13.52,15.39,17.25,19.309999999999999,21.27,23.23,25.48,27.93,30.38,32.83,35.770000000000003,38.22,41.16,44.1,47.04,50.96,53.9,56.84,59.78,62.72,66.64]
[null,"P","Qø","d","v","I1","dp","p","p",null,null,null,null,null,null,null,null,null,null,25,null,null,null,null,null,null,null,null,null,null,null,1.76,1.27,1.47,1.67,1.86,2.06,2.2999999999999998,2.5,2.74,3.04,3.33,3.58,3.87,4.17,4.51,4.8,5.0999999999999996,5.49,6.17,6.96,7.74,8.5299999999999994,9.51,10.49,11.27,12.35,13.43,14.5,15.68,16.95,17.93,19.11,20.58,22.05,23.03,24.5,25.97,26.46,31.36,35.28,40.18,44.1,49,53.9]
[null,"kW","m³/h","mm","m/s","m","mbar","mbar","mbar",null,null,null,null,null,null,null,null,null,null,null,"Tryktab i Pa"]
[null,null,{"$f":"B12/5.93","v":0},null,{"$f":"IFERROR(4*C12/(3600*3.1415*POWER(IF(D12=10,0.0115,IF(D12=15,0.015,IF(D12=20,0.0208,IF(D12=25,0.025)))),2)),\"\")","v":""},null,{"$f":"HLOOKUP(C12,T15:BW19,T22,TRUE)","v":{"$error":"#N/A"}},{"$f":"F12*G12","v":{"$error":"#N/A"}},{"$f":"H12","v":{"$error":"#N/A"}},null,"Det samlede tryktab må normalt ikke overstige:",null,null,null,null,null,null,null,null,"Naturgas"]
[null,null,0,null,"",null,{"$f":"HLOOKUP(C13,T15:BW19,T23,TRUE)","v":{"$error":"#N/A"}},{"$f":"F13*G13","v":{"$error":"#N/A"}},{"$f":"I12+H13","v":{"$error":"#N/A"}},null,"Trykniveau 22 mbar: 2 mbar frem til apparaterne"]
[null,null,0,null,"",null,{"$f":"HLOOKUP(C14,T15:BW19,T24,TRUE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$f":"I13+H14","v":{"$error":"#N/A"}},null,"Trykniveau 50 - 100 mbar: 5 mbar",null,null,null,null,null,null,null,null,"Dimension [mm]","Flow [m³/h]"]
[null,null,0,null,"",null,{"$f":"HLOOKUP(C15,T15:BW19,T25,TRUE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,null,null,null,null,null,null,null,{"$f":"U6/0.9","v":0.22222222222222224},{"$f":"V6/0.9","v":0.33333333333333331},0.44444444444444448,0.55555555555555558,0.66666666666666663,0.77777777777777768,0.88888888888888895,1,1.1111111111111112,1.2222222222222223,1.3333333333333333,1.4444444444444444,1.5555555555555554,1.6666666666666665,1.7777777777777779,1.8888888888888888,2,2.1111111111111112,2.2222222222222223,2.3333333333333335,2.4444444444444446,2.5555555555555554,2.6666666666666665,2.7777777777777777,2.8888888888888888,3,3.1111111111111107,3.2222222222222219,3.333333333333333,3.5555555555555558,3.7777777777777777,4,4.2222222222222223,4.4444444444444446,4.666666666666667,4.8888888888888893,5.1111111111111107,5.333333333333333,5.5555555555555554,5.7777777777777777,6,6.2222222222222214,6.4444444444444438,6.6666666666666661,6.8888888888888893,7.1111111111111116,7.333333333333333,7.5555555555555554,7.777777777777767,8.3333333333333339,8.8888888888888893,9.4444444444444446,10,10.555555555555555,11.111111111111111]
[null,null,0,null,"",null,{"$f":"HLOOKUP(C16,T15:BW19,T26,TRUE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,null,null,null,null,null,null,10,{"$f":"ROUND(U7/100,2)","v":0.02},{"$f":"ROUND(V7/100,2)","v":0.02},0.04,0.05,0.1,0.15,0.2,0.25,0.32,0.39,0.47,0.56000000000000005,0.67,0.77,"Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl"]
[null,null,0,null,"",null,{"$f":"HLOOKUP(C17,T15:BW19,T27,TRUE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,null,null,null,null,null,null,15,null,{"$f":"ROUND(V8/100,2)","v":0.01},0.01,0.02,0.02,0.03,0.04,7.0000000000000007E-2,0.09,0.11,0.13,0.15,0.17,0.2,0.22,0.25,0.28000000000000003,0.31,0.34,0.37,0.41,0.45,0.49,0.52,0.56999999999999995,0.61,0.65,0.7,0.74,"Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl","Fejl"]
[null,null,0,null,"",null,{"$f":"HLOOKUP(C18,T15:BW19,T28,TRUE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,null,null,null,null,null,null,20,null,null,null,null,null,null,{"$f":"ROUND(AA9/100,2)","v":0.01},0.01,0.01,0.02,0.02,0.02,0.03,0.04,0.04,0.05,0.05,0.06,0.06,7.0000000000000007E-2,0.08,0.08,0.09,0.1,0.1,0.11,0.12,0.13,0.14000000000000001,0.15,0.17,0.19,0.21,0.23,0.25,0.28000000000000003,0.3,0.33,0.36,0.38,0.41,0.44,0.47,0.51,0.54,0.56999999999999995,0.6,0.63,0.67,"Fejl","Fejl","Fejl","Fejl","Fejl","Fejl"]
[null,null,0,null,"",null,{"$f":"HLOOKUP(C19,T15:BW19,T29,TRUE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,null,null,null,null,null,null,25,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(AF10/100,2)","v":0.02},0.01,0.01,0.02,0.02,0.02,0.02,0.03,0.03,0.03,0.03,0.04,0.04,0.04,0.05,0.05,0.05,0.05,0.06,7.0000000000000007E-2,0.08,0.09,0.1,0.1,0.11,0.12,0.13,0.15,0.16,0.17,0.18,0.19,0.21,0.22,0.23,0.25,0.26,0.26,0.31,0.35,0.4,0.44,0.49,0.54]
[null,null,0,null,"",null,{"$f":"HLOOKUP(C20,T15:BW19,T30,TRUE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,null,null,null,null,null,null,null,"Tryktab i mbar"]
[]
["Gastype:    Bygas2",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(D12=10,2,IF(D12=15,3,IF(D12=20,4,IF(D12=25,5,0))))","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
["Beregningsgrundlag:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
["Tryktabellen (side 9) Projekterings- og installationsvejledning, dateret September 2003 fra fabrikanten: Kyosei & Co., LTD. \nDansk rep.: Hiramatsu Company ApS, Sundsvej 55, 8700 Horsens\n\nAlle tal for tryktab inkluderer påvirkningen af en bøjning med en bøjningsradius på 50 mm for hver 2 meter ledningsstrækning.\n\nProgrammet kan kun anvendes til Bygas2 med øvre brændværdi 5,93 kWh/m³ og relativ massefylde 0,81.\n\nCopyright: De danske gasselskaber",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
["Størrelse og dimensioner:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
["Nominel størrelse i mm",null,10,15,20,25,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
["Indvendig diameter",null,"11,5 mm","15,0 mm","20,8 mm","25,0 mm",null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]

{"sheet":"Ark2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Ark3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}